AB  Axis Industries

SKS4 communication protocol description

Kaunas  2007

Table of contents

1	Introduction	2

2	Technological protocol	2

2.1	Reading of internal controller memory	2

2.2	Writing to internal controller memory	3

2.3	Erase of menu FLASH memory area	3

2.4	Reading of external FLASH memory	3

2.5	Writing to external FLASH memory	3

3	Reading/setting of relay parameters	4

3.1	Reading of relay parameters	4

3.2	Setting the relay parameters	5

4	Reading of meter configuration	6

5	Reading of integral and moment parameters	6

5.1	Energy	11

5.2	Amounts	11

5.3	Masses	11

5.4	Power	11

5.5	Flows	12

5.6	Temperatures	12

5.7	Pressures	12

5.8	Date/time	12

5.9	Error code	12

5.10	Power supply duration	13

5.11	Normal working time	13

6	Readout of hours and days archive	13

6.1	Energy	14

6.2	Amounts	15

6.3	Masses	15

6.4	Temperatures	15

6.5	Pressures	15

6.6	Record date/time	15

6.7	Error code	16

6.8	Power supply duration	16

6.9	Normal working time	16

7	Month and year report days archive readout	16

7.1	Energy	17

7.2	Amounts	18

7.3	Masses	18

7.4	Record date/time	18

7.5	Normal working time	18

8	Read/set of T3 constant	18

8.1	T3 constant readout	19

8.2	Setting the T3 constant	19

9	Clock readout/setting in normal mode	20

9.1	Clock readout	20

9.2	Clock setting	21

10	Secondary addressing	21

# Introduction

M-bus protocol of SKS-4 has following groups::

- Technological protocol

- Read/set relay parameters

- Reading of meter configuration

- Read/set T3 constant

- Reading of integral and moment parameters

- Reading of hours archive

- Reading of day archive

- Reading of month report days archive

- Reading of year report days archive

Further, in description of packets, these abbreviations are used:

| A | M-bus address |
| --- | --- |
| L | M-bus packet length |
| CS | M-bus control sum |
| No0, No1, No2, No3 | Customer code in BCD representation |
| Acc | M-bus parameter “Access number”, which is incremented in each packed from slave |

# Technological protocol

Technological protocol is permissible only when meter is in SET or TEST mode or in all modes when jumper X5 is on.

## Reading of internal controller memory

Master sends following packet:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 0Ah | 0Ah | 68h | 53h | A | A1h | 0Fh | 00h | Len | Addr |  |  |  | CS | 16h |

Where Len is length of data block, Addr is start address of memory block.

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 – (n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | A1h | 0Fh | Data (memory contents) | CS | 16h |
|  |  |  |  | L bytes |  |  |  |  |  |  |

The reading is allowed only for RAM and menu info area.

## Writing to internal controller memory

Master sends following packet to meter with data to write:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 – (n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 53h | A | A2h | 0Fh | 00h | Addr |  |  |  | Data to be written to memory | CS | 16h |
|  |  |  |  | L bytes |  |  |  |  |  |  |  |  |  |  |  |

Where Addr is start address of memory block.

Answer of the meter:

0

E5h

## Erase of menu FLASH memory area

Master sends following packet:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 05h | 05h | 68h | 53h | A | A2h | 0Fh | 03h | CS | 16h |

Answer of the meter:

0

E5h

## Reading of external FLASH memory

Master sends following packet:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 0Ah | 0Ah | 68h | 53h | A | A1h | 0Fh | 02h | Len | Addr |  |  |  | CS | 16h |

Where Len is length of data block, Addr is start address of memory block.

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 – (n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | A1h | 0Fh | Data (memory contents) | CS | 16h |
|  |  |  |  | L bytes |  |  |  |  |  |  |

## Writing to external FLASH memory

Master sends following packet to meter with data to write:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 – (n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 53h | A | A2h | 0Fh | 02h | Addr |  |  |  | Data to be written to memory | CS | 16h |
|  |  |  |  | L bytes |  |  |  |  |  |  |  |  |  |  |  |

Where Addr is start address of memory block.

Answer of the meter:

0

E5h

# Reading/setting of relay parameters

## Reading of relay parameters

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

Then the selection of relay parameters is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 05h | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 1Eh | 1Eh | 68h | 08h | A | 72h | No0 | No1 | No2 | No3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | 0Fh | 00h | RelP | Max0 | Max1 | Max2 | Max3 | Min0 | Min1 | Min2 | Min3 |
|  |  |  |  |  |  |  | Max |  |  |  | Min |  |  |  |

| 30 | 31 | 32 | 33 | 34 | 35 |
| --- | --- | --- | --- | --- | --- |
| Con0 | Con1 | Dis0 | Dis1 | CS | 16 |
| Con |  | Dis |  |  |  |

Where:

| RelP | Relay parameter: Bits. 7; 6; 5; 4; 3; 2; 1; 0. 0 – relay is off 1 – relay is on; 00h – Power 01h – 1st temperature 02h – 2nd temperature 03h – difference of the 1st and 2nd temperature 04h – 3rd temperature 05h – 1st flow 06h – 2nd flow 07h – difference ot the 1st and the 2nd flow 08h – 3rd flow 09h – 4th flow 0Ah – 1st pressure 0Bh – 2nd pressure. |
| --- | --- |
| Max | Max relay value (in standard 32-bit IEEE float format) |
| Min | Min relay value (in standard 32-bit IEEE float format) |
| Con | Connect time (integer value in 0.1 seconds) |
| Dis | Disconnect time (integer value in 0.1 seconds) |

## Setting the relay parameters

Master sends following packet:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 12h | 12h | 68h | 53h | A | 51h | 0Fh | 00h | RelP | Max0 | Max1 | Max2 | Max3 |
|  |  |  |  |  |  |  |  |  |  | Max |  |  |  |

| 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Min0 | Min1 | Min2 | Min3 | Con0 | Con1 | Dis0 | Dis1 | CS | 16 |
| Min |  |  |  | Con |  | Dis |  |  |  |

Where:

| RelP | Relay parameter: Bits. 7; 6; 5; 4; 3; 2; 1; 0. 0 – relay is off 1 – relay is on; 00h – Power 01h – 1st temperature 02h – 2nd temperature 03h – difference of the 1st and 2nd temperature 04h – 3rd temperature 05h – 1st flow 06h – 2nd flow 07h – difference ot the 1st and the 2nd flow 08h – 3rd flow 09h – 4th flow 0Ah – 1st pressure 0Bh – 2nd pressure. |
| --- | --- |
| Max | Max relay value (in standard 32-bit IEEE float format) |
| Min | Min relay value (in standard 32-bit IEEE float format) |
| Con | Connect time (integer value in 0.1 seconds) |
| Dis | Disconnect time (integer value in 0.1 seconds) |

Answer of the meter:

0

E5h

# Reading of meter configuration

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

Then the selection of configuration parameters is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 06h | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | 72h | No0 | No1 | No2 | No3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19 | 20 | 21-(n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | 0Fh | 01h | Configuration of the meter | CS | 16 |

| Offset in bytes | Size in bytes | Format | Parameter |
| --- | --- | --- | --- |
| 0 | 4 | Unsigned integer | Serial number |
| 4 | 4 | Unsigned integer | Customer code |
| 8 | 4 | Unsigned integer | Battery change date (seconds since 2004.01.01 00:00) |
| 12 | 1 | Unsigned integer | Year review date month |
| 13 | 1 | Unsigned integer | Year review date day |
| 14 | 1 | Unsigned integer | Year review date hour |
| 15 | 1 | Unsigned integer | Year review date minute |
| 16 | 1 | Unsigned integer | Year review period parameters zero (0-no, 1-yes) |
| 17 | 1 | Unsigned integer | Month review date month (not used) |
| 18 | 1 | Unsigned integer | Month review date day |
| 19 | 1 | Unsigned integer | Month review date hour |
| 20 | 1 | Unsigned integer | Month review date minute |
| 21 | 1 | Unsigned integer | Month review period parameters zero (0-no, 1-yes) |
| 22 | 4 | IEEE float | V1 pulse value m3/pulse |
| 26 | 4 | IEEE float | V2 pulse value m3/pulse |
| 30 | 4 | IEEE float | V3 pulse value m3/pulse |
| 34 | 4 | IEEE float | V4 pulse value m3/pulse |
| 38 | 4 |  | Calibration data |
| 42 | 1 | Unsigned integer | M-bus address |
| 43 | 1 |  | Wire interface baud rate |
| 44 | 1 | Unsigned integer | Temperature sensor type and measurement scheme |
| 45 | 1 |  | Not used |
| 46 | 1 |  | V1 input type |
| 47 | 1 |  | Not used |
| 48 | 2 | Unsigned integer | V1 maximal frequency in Hz |
| 50 | 1 |  | V2 input type |
| 51 | 1 |  | Not used |
| 52 | 2 | Unsigned integer | V2 maximal frequency in Hz |
| 54 | 1 |  | V3 input type |
| 55 | 1 |  | Not used |
| 56 | 2 | Unsigned integer | V3 maximal frequency in Hz |
| 58 | 1 |  | V4 input type |
| 59 | 1 |  | Not used |
| 60 | 2 | Unsigned integer | V4 maximal frequency in Hz |
| 62 | 4 |  | Not used |
| 66 | 2 | Integer | Cold water (T3) constant in 0.01’C |
| 68 | 1 | Unsigned integer | T3 measure (0-use T3 constant, 1-measure T3) |
| 69 | 1 |  | Not used |
| 70 | 1 |  | Heat liquid type |
| 71 | 1 |  | Not used |
| 72 | 1 | Unsigned integer | 1st pressure input type |
| 73 | 1 | Unsigned integer | 2nd pressure input type |
| 74 | 2 | Unsigned integer | 1st pressure input maximal value in 0.1kPa |
| 76 | 2 | Unsigned integer | 2nd pressure input maximal value in 0.1kPa |
| 78 | 1 |  | Printing language |
| 79 | 1 | Unsigned integer | 1st pulse output type |
| 80 | 1 | Unsigned integer | 2nd pulse output type |
| 81 | 1 |  | Relay output parameter |
| 82 | 4 | IEEE float | Relay max value |
| 86 | 4 | IEEE float | Relay min value |
| 90 | 8 |  | Calibration data |
| 98 | 2 | Unsigned integer | Relay connect time in 0.1s |
| 100 | 2 | Unsigned integer | Relay disconnect time in 0.1s |
| 102 | 4 | IEEE float | 1st tariff limit value |
| 106 | 1 | Unsigned integer | 1st tariff “from hour” |
| 107 | 1 | Unsigned integer | 1st tariff “to hour” |
| 108 | 1 |  | 1st tariff parameter |
| 109 | 1 |  | 1st tariff parameter bounds (0-lower, 1-upper) |
| 110 | 4 | IEEE float | 2nd tariff limit value |
| 114 | 1 | Unsigned integer | 2nd tariff “from hour” |
| 115 | 1 | Unsigned integer | 2nd tariff “to hour” |
| 116 | 1 |  | 2nd tariff parameter |
| 117 | 1 |  | 2nd tariff parameter bounds (0-lower, 1-upper) |
| 118 | 1 |  | Dimension units |
| 119 | 1 |  | Not used |
| 120 | 12 |  | Calibration data |

Temperature sensor type and measurement scheme:

| Bits |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
| Temperature sensor type: 0 – Pt500 1 – Pt1000 2 – 500П 3 – 1000П |  |  |  |  |  | Measurement scheme: 0 – “R” 1 – “R1” 2 – “F” 3 – “O” |  |

Flow input type:

| Bits |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
| Input filter: 0 – off 1 - on | Input type: 0 – off 1 – “S” type 2 – “E” type 3 – “B” type 4 – “H” type |  |  |  |  |  |  |

Heat liquid type:

| Value | Type |
| --- | --- |
| 0 | Water |
| 1 | Norcorsin 10 |
| 2 | Norcorsin 20 |
| 3 | Norcorsin 30 |
| 4 | Norcorsin 40 |
| 5 | Norcorsin 50 |
| 6 | Norcorsin 60 |
| 7 | Antifrogen L16 |
| 8 | Antifrogen L25 |
| 9 | Antifrogen L38 |
| 10 | Antifrogen L47 |
| 11 | Antifrogen N20 |
| 12 | Antifrogen N34 |
| 13 | Antifrogen N44 |
| 14 | Antifrogen N52 |
| 15 | PKL 90 |
| 16 | PKL 300 |

Pressure input type:

| Value | Type |
| --- | --- |
| 0 | Off |
| 1 | 0-20 mA |
| 2 | 4-20 mA |
| 3 | 0-5 mA |

Printing language:

| Value | Language |
| --- | --- |
| 0 | English |
| 1 | Germany |
| 2 | Regional |

Pulse output parameter

| Value | Parameter |
| --- | --- |
| 0 | Off |
| 1 | Energy |
| 2 | 1st tariff energy |
| 3 | 2nd tariff energy |
| 4 | 1st volume |
| 5 | 2nd volume |
| 6 | 3rd volume |
| 7 | 4th volume |

Relay output parameter:

| Bits |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
| Relay on/off: 0-off 1-on | Relay parameter: 0 – power 1 – 1st temetrature 2 – 2nd temperature 3 – temperature difference T1-T2 4 – 3rd temperature 5 – 1st flow 6 – 2nd flow 7 – flow difference q1-q2 8 – 3rd flow 9 – 4th flow 10 – 1st pressure 11 – 2nd pressure |  |  |  |  |  |  |

Tariff parameter:

| Value | Parameter |
| --- | --- |
| 0 | Off |
| 1 | Power |
| 2 | 1st flow |
| 3 | 2nd flow |
| 4 | Flow difference q1-q2 |
| 5 | 3rd flow |
| 6 | 4th flow |
| 7 | 1st temperature |
| 8 | 2nd temperature |
| 9 | Temperature difference T1-T2 |
| 10 | 3rd temperature |
| 11 | 1st pressure |
| 12 | 2nd pressure |
| 13 | Pressure difference p1-p2 |
| 14 | Clock (hours from-to) |

Dimension units:

| Bits |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 |
| Energy dimension units: 0 – MWh or kWh 1 – Gcal 2 - GJ |  | Reserved |  |  |  |  |  |

# Reading of integral and moment parameters

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

Then the selection of integral and moment parameters is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 00h | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | 72h | No0 | No1 | No2 | No3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19-(n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | Integral and moment parameters block | CS | 16h |

In the block of integral moment parameters can be following parameters (depending on configuration of the meter):

- Energy

- 1st tariff energy

- 2nd tariff energy

- 1st amount

- 2nd amount

- 3rd amount

- 4th amount

- 1st mass

- 2nd mass

- Power

- 1st flow

- 2nd flow

- 3rd flow

- 4th flow

- 1st temperature

- 2nd temperature

- 3rd temperature

- 1st pressure

- 2nd pressure

Also, independently of configuration, following parameters are in the block:

- Current date/time of the meter

- Error code

- Power supply duration

- Normal working time

## Energy

| Parameter | DIB | VIB |  |  |  |  |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0,1 MWh | 0,1 GJ | 0,01 MWh | 0,01 GJ | 0,001 MWh | 0,001 GJ | 0,0001 MWh | 0,0001 GJ |  |
| Energy | 04 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |
| 1st tariff energy | 84 10 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |
| 2nd tariff energy | 84 20 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long) |

## Amounts

| Parameter | DIB | VIB |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 m3 | 0,1 m3 | 0,01 m3 | 0,001 m3 |  |
| 1st amount | 04 | 16 | 15 | 14 | 13 | 4 bytes (long) |
| 2nd amount | 84 40 | 16 | 15 | 14 | 13 | 4 bytes (long) |
| 3rd amount | 84 80 40 | 16 | 15 | 14 | 13 | 4 bytes (long) |
| 4th amount | 84 C0 40 | 16 | 15 | 14 | 13 | 4 bytes (long) |

## Masses

| Parameter | DIB | VIB |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 t | 0,1 t | 0,01 t | 0,001 t |  |
| 1st mass | 04 | 1E | 1D | 1C | 1B | 4 bytes (long) |
| 2nd mass | 84 40 | 1E | 1D | 1C | 1B | 4 bytes (long) |

## Power

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Power | 05 | 2E | 4 bytes (IEEE float) kW |

## Flows

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| 1st flow | 05 | 3E | 4 bytes (IEEE float) m3/h |
| 2nd flow | 85 40 | 3E | 4 bytes (IEEE float) m3/h |
| 3rd flow | 85 80 40 | 3E | 4 bytes (IEEE float) m3/h |
| 4th flow | 85 C0 40 | 3E | 4 bytes (IEEE float) m3/h |

## Temperatures

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| 1st temperature | 02 | 59 | 2 bytes (integer), 0,01oC |
| 2nd temperature | 02 | 5D | 2 bytes (integer) 0,01oC |
| 3rd temperature | 82 40 | 59 | 2 bytes (integer) 0,01oC |

## Pressures

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| 1st pressure | 03 | 68 | 3 bytes (integer) 0,1 kPa |
| 2nd pressure | 83 40 | 68 | 3 bytes (integer) 0,1 kPa |

## Date/time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Date/time | 44 | 6D | 4 bytes (date/time format) |

Format of date/time is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Year1 |  |  |  | Month |  |  |  | Year0 |  |  | Day |  |  |  |  | 0 | 0 | 0 | Hour |  |  |  |  | 0 | 0 | Minutes |  |  |  |  |  |

Minutes - <0 to 59>

Hour - <0 to 23>

Day - <1 to 31>

Month - <1 to 12>

Year=Year1|Year0 (Year0 – low significant part, Year1 – high significant part) <0 to 99>

## Error code

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Error code | 04 | FD 17 | 4 bytes (error code format) |

Format of error code is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Not used |  |  |  |  |  |  |  |  |  |  |  |  | V3,V4, meter error |  |  |  | V2 error |  |  | V1 error |  |  | T3 error |  |  | T2 error |  |  | T1 error |  |  |

## Power supply duration

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Power supply duration | 04 | 20 | 4 bytes (long integer, time in seconds) |

## Normal working time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Normal working time | 04 | 24 | 4 bytes (long integer, time in seconds) |

# Readout of hours and days archive

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

Then the selection of hours or days archive is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 04h – for hours archive 03h – for days archive | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | 72h | No0 | No1 | No2 | No3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19-(n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | Hours/days archive record block | CS | 16h |

The readout of the next record of the archive is performed by sending data query packet with changed 1st byte 5Bh/7Bh (toggling the most significant bit of the byte). Archive readout is performed from the newest records.

In the block of hours and days archive can be following parameters (depending on meter configuration):

- Energy

- 1st tariff energy

- 2nd tariff energy

- 1st amount

- 2nd amount

- 3rd amount

- 4th amount

- 1st mass

- 2nd mass

- 1st average temperature

- 2nd average temperature

- 3rd average temperature

- 1st average pressure

- 2nd average pressure

Also, independently of configuration, following parameters are in the block:

- Date/time of record

- Error code (sum for day or hour)

- Power supply duration

- Normal working time

## Energy

| Parameter | DIB | VIB |  |  |  |  |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0,1 MWh | 0,1 GJ | 0,01 MWh | 0,01 GJ | 0,001 MWh | 0,001 GJ | 0,0001 MWh | 0,0001 GJ |  |
| Energy | 04 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long integer) |
| 1st tariff energy | 84 10 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long integer) |
| 2nd tariff energy | 84 20 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long integer) |

## Amounts

| Parameter | DIB | VIB |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 m3 | 0,1 m3 | 0,01 m3 | 0,001 m3 |  |
| 1st amount | 04 | 16 | 15 | 14 | 13 | 4 bytes (long integer) |
| 2nd amount | 84 40 | 16 | 15 | 14 | 13 | 4 bytes (long integer) |
| 3rd amount | 84 80 40 | 16 | 15 | 14 | 13 | 4 bytes (long integer) |
| 4th amount | 84 C0 40 | 16 | 15 | 14 | 13 | 4 bytes (long integer) |

## Masses

| Parameter | DIB | VIB |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 t | 0,1 t | 0,01 t | 0,001 t |  |
| 1st mass | 04 | 1E | 1D | 1C | 1B | 4 bytes (long integer) |
| 2nd mass | 84 40 | 1E | 1D | 1C | 1B | 4 bytes (long integer) |

## Temperatures

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| 1st temperature | 02 | 59 | 2 bytes (integer), 0,01oC |
| 2nd temperature | 02 | 5D | 2 bytes (integer) 0,01oC |
| 3rd temperature | 82 40 | 59 | 2 bytes (integer) 0,01oC |

## Pressures

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| 1st pressure | 03 | 68 | 3 bytes (integer) 0,1 kPa |
| 2nd pressure | 83 40 | 68 | 3 bytes (integer) 0,1 kPa |

## Record date/time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Record date/time | 44 | 6D | 4 bytes (date/time format) |

The format of date/time is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Year1 |  |  |  | Month |  |  |  | Month0 |  |  | Day |  |  |  |  | 0 | 0 | 0 | Hour |  |  |  |  | 0 | 0 | Minutes |  |  |  |  |  |

Minutes - <0 to 59>

Hour - <0 to 23>

Day - <1 to 31>

Month - <1 to12>

Year=Year1|Year0 (Year0 – low significant part, Year1 – high significant part) <0 to 99>

## Error code

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Error code | 04 | FD 17 | 4 bytes (error code format) |

The format of error code is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Not used |  |  |  |  |  |  |  |  |  |  |  |  | V3,V4, meter error |  |  |  | V2 error |  |  | V1 error |  |  | T3 error |  |  | T2 error |  |  | T1 error |  |  |

## Power supply duration

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Power supply duration | 04 | 20 | 4 bytes (long integer, time in seconds) |

## Normal working time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Normal working time | 04 | 24 | 4 bytes (long integer, time in seconds) |

# Month and year report days archive readout

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Answer of the meter:

0

E5h

Then the selection of month or year report days archive is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 02h – for month report days archive 01h – for year report days archive | CS | 16h |

Answer of the meter:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Answer of the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | L | L | 68h | 08h | A | 72h | No0 | No1 | No2 | No3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19-(n-2) | n-1 | n |
| --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | Block of month/year archive parameters | CS | 16h |

The readout of the next record of the archive is performed by sending data query packet with changed 1st byte 5Bh/7Bh (toggling the most significant bit of the byte). Archive readout is performed from the newest records.

In the block of month and year report days archive can be following parameters (depending on meter configuration):

- Energy

- 1st tariff energy

- 2nd tariff energy

- 1st amount

- 2nd amount

- 3rd amount

- 4th amount

- 1st mass

- 2nd mass

Also, independently of configuration, following parameters are in the block:

- Record date/time

- Normal working time

## Energy

| Parameter | DIB | VIB |  |  |  |  |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0,1 MWh | 0,1 GJ | 0,01 MWh | 0,01 GJ | 0,001 MWh | 0,001 GJ | 0,0001 MWh | 0,0001 GJ |  |
| Energy | 04 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long integer) |
| 1st tariff energy | 84 10 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long integer) |
| 2nd tariff energy | 84 20 | FB 00 | FB 08 | 07 | 0F | 06 | 0E | 05 | 0D | 4 bytes (long integer) |

## Amounts

| Parameter | DIB | VIB |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 m3 | 0,1 m3 | 0,01 m3 | 0,001 m3 |  |
| 1-as amount | 04 | 16 | 15 | 14 | 13 | 4 bytes (long integer) |
| 2-as amount | 84 40 | 16 | 15 | 14 | 13 | 4 bytes (long integer) |
| 3-as amount | 84 80 40 | 16 | 15 | 14 | 13 | 4 bytes (long integer) |
| 4-as amount | 84 C0 40 | 16 | 15 | 14 | 13 | 4 bytes (long integer) |

## Masses

| Parameter | DIB | VIB |  |  |  | Data |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 t | 0,1 t | 0,01 t | 0,001 t |  |
| 1st mass | 04 | 1E | 1D | 1C | 1B | 4 bytes (long integer) |
| 2nd mass | 84 40 | 1E | 1D | 1C | 1B | 4 bytes (long integer) |

## Record date/time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Date/time | 44 | 6D | 4 bytes (date/time format) |

Format of date/time is following:

| Bytes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3 |  |  |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| Bits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 09 | 08 | 07 | 06 | 05 | 04 | 03 | 02 | 01 | 00 |
| Year1 |  |  |  | Month |  |  |  | Year0 |  |  | Day |  |  |  |  | 0 | 0 | 0 | Hour |  |  |  |  | 0 | 0 | Minutes |  |  |  |  |  |

Minutes - <0 to 59>

Hour - <0 to 23>

Day - <1 to 31>

Month - <1 to 12>

Year=Year1|Year0 (Year0 – low significant part, Year1 – high significant part) <0 to 99>

## Normal working time

| Parameter | DIB | VIB | Data |
| --- | --- | --- | --- |
| Normal working time | 04 | 24 | 4 bytes (long integer, time in seconds) |

# Read/set of T3 constant

This functionality is only present in IC5

## T3 constant readout

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Meter answer:

0

E5h

Then the selection of T3 constant is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 17h | CS | 16h |

Meter answer:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Meter answer:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 1Bh | 1Bh | 68h | 08h | A | 72h | No0 | No1 | No2 | No3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | 0Fh | 02h | N0 | N1 | N2 | N3 | Cl0 | Cl1 | Cl2 | Cl3 |

| 29 | 30 | 31 | 32 |
| --- | --- | --- | --- |
| T3const0 | T3const1 | CS | 16h |

N0, N1, N2, N3 – meter serial number bytes (they make serial number, N0 – least significant byte of the number, N3 – most significant byte of the number).

Cl0, Cl1, Cl2, Cl3 – internal meter clock, which is used in generation of security code (Cl0 – least significant byte, Cl3 – most significant byte). Clock is calculated in seconds past 2004.01.01 00:00.

T3const0, T3const1 – T3 constant (T3const0 – least significant byte, T3const1 – most significant byte).

## Setting the T3 constant

Master sends data packet:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 0Bh | 0Bh | 68h | 53h | A | A3h | 0Fh | 0Bh | Sec0 | Sec1 | Sec2 | Sec3 |

| 13 | 14 | 15 | 16 |
| --- | --- | --- | --- |
| T3const0 | T3const1 | CS | 16h |

Sec0, Sec1, Sec2, Sec3 – security code (Sec0 – least significant byte, Sec3 – most significant byte).

T3const0, T3const1 – T3 constant (T3const0 – least significant byte, T3const1 – most significant byte).

Answer of the meter:

0

E5h

# Clock readout/setting in normal mode

This functionality is only present in IC5

## Clock readout

First is SND_NKE / E5 negotiation is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 40h | A | CS | 16h |

Meter answer:

0

E5h

Then the selection of clock data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 04h | 04h | 68h | 53h | A | 50h | 18h | CS | 16h |

Meter answer:

0

E5h

Then the query for data is performed. Master sends to the meter:

| 0 | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| 10h | 5B/7B | A | CS | 16 |

Meter answer:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 1Dh | 1Dh | 68h | 08h | A | 72h | No0 | No1 | No2 | No3 | 34h | 2Ch | 03h | 04h |

| 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Acc | 00h | 00h | 00h | 0Fh | 03h | N0 | N1 | N2 | N3 | Cl0 | Cl1 | Cl2 | Cl3 |

| 29 | 30 | 31 | 32 | 33 | 34 |
| --- | --- | --- | --- | --- | --- |
| Clock0 | Clock1 | Clock2 | Clock3 | CS | 16h |

N0, N1, N2, N3 – meter serial number bytes (they make serial number, N0 – least significant byte of the number, N3 – most significant byte of the number).

Cl0, Cl1, Cl2, Cl3 – internal meter clock, which is used in generation of security code (Cl0 – least significant byte, Cl3 – most significant byte). Clock is calculated in seconds past 2004.01.01 00:00.

Clock0, Clock1, Clock2, Clock3 – Meter clock (Clock0 – least significant byte, Clock3 – most significant byte). Clock is calculated in seconds past 2004.01.01 00:00

## Clock setting

Master sends data packet:

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68h | 0Dh | 0Dh | 68h | 53h | A | A3h | 0Fh | 0Ch | Sec0 | Sec1 | Sec2 | Sec3 |

| 13 | 14 | 15 | 16 | 17 | 18 |
| --- | --- | --- | --- | --- | --- |
| Clock0 | Clock1 | Clock2 | Clock3 | CS | 16h |

Sec0, Sec1, Sec2, Sec3 – security code (Sec0 – least significant byte, Sec3 – most significant byte).

Clock0, Clock1, Clock2, Clock3 – Meter clock (Clock0 – least significant byte, Clock3 – most significant byte). Clock is calculated in seconds past 2004.01.01 00:00

Meter answer:

0

E5h

# Secondary addressing

Meter supports secondary addressing. The address of secondary addressing is meter parameter “Serial number” (Number), and most significant digit of address splits meter in to four sub-meters.

If meter with number “Number”  is selected, parameters are coded the same as in primary addressing.

If meter with number (10000000+ Number) is selected, parameters V2, M2, q2, T2, p2 are coded as V1, M1, q1, T1, p1 ( only when transmitting parameters V2 (M2) is activated).

If meter with number (20000000+ Number) is selected, parameters V3, q3 are coded as V1, q1   (only when transmitting parameter V3 is activated).

If meter with number (30000000+ Number) is selected, parameters V4, q4 are coded as V1, q1   (only when transmitting parametersV3 is activated).